## Menu
FlexCalculator Suite
Battery Size
Standby Time
Voltage Drop
Wire Size
Ohm's Law
Misc Calcs
B100 Calc
C4/C8 Config

## Battery Size Calc
Battery Size Calculator
Standby Load |  |  |  | Required Backup Time
| DC1 |  | Amps |  | Hours |  | Minutes |  | Total
| DC2 |  | Amps | Standby |  | : |  | = | 0 | Hours
| Accessory Boards |  | Amps
| Total Standby Load | 0 | Amps | Alarm |  | : |  | = | 0 | Hours
Alarm Load |  |  |  | Result
[7 empty] | Standby AH |  | 0 | AH
| DC1 |  | Amps |  |  |  | Alarm AH |  | 0 | AH
| DC2 |  | Amps |  |  |  | Minimum Total AH |  | 0 | AH
| Accessory Boards |  | Amps |  |  |  | Safety Factor |  | 20 | %
| Total Alarm Load | 0 | Amps |  |  |  | Recommended Battery |  | 0 | AH
Notes:
Job:
Location:
Power Supply ID:
Date: | 2014-12-15
Help
Help
Calculate
Main Menu

## Battery Size Help
Help for Battery Size Calculator
The Battery Size Calculator calculates the minimum battery required for a system based on current and time. It uses Peukert's law to calculate an accurate battery requirement based on rate of discharge.
Step 1: | Enter the standby load values in amperes into the blue cells in the "Standby Load" box. Spaces for DC1, DC2, and total accessory board loading are provided. Be sure to add the standby load of the FPO board to the DC1 Current (See the instruction manual for the standby load of the FPO model you are using).
Step 2: | Enter the alarm load values in to the red cells in the "Alarm Load" box. If there is no Alarm Current, leave these cells blank.
Step 3: | Enter the required Standby and Alarm times into the blue and red cells in the "Required Backup Time box. If there is no Alarm Time, leave these cells blank.
Step 4: | (Optional) Enter a Safety Factor into the purple cell in the "Results" box. This is to take into account the gradual decrease in AH capacity of a battery as it ages.
Step 5: | Click the blue "Calculate" button. The recommended battery size appears in the green cell in the "Results" box.
Back

## Standby Time Calc
Standby Time Calculator
Standby Load |  |  |  | Battery Size & Required Alarm Time
| DC1 |  | Amps |  | Installed Battery Size |  |  | = |  | AH
| DC2 |  | Amps
| Accessory Boards |  | Amps |  | Hours |  | Minutes |  | Total
| Total Standby Load | 0 | Amps | Alarm |  | : |  | = | 0 | Hours
Alarm Load |  |  |  | Result
| DC1 |  | Amps | Alarm AH Required |  |  |  | = | 0 | AH
| DC2 |  | Amps | Standby AH Remaining |  |  |  | = | 0 | AH
| Accessory Boards |  | Amps
| Total Alarm Load | 0 | Amps | Expected Standby Time |  |  |  | = | Error | Hours
Notes:
Job:
Location:
Power Supply ID:
Date: | 2014-12-15
Help
Help
Calculate
Main Menu

## Standby Time Help
Help for Standby Time Calculator
The Standby Time Calculator calculates the available standby time for a given current and load. It uses Peukert's law to calculate an accurate standby time based on rate of discharge.
Step 1: | Enter the standby load values in amperes into the blue cells in the "Standby Load" box. Spaces for DC1, DC2, and total accessory board loading are provided. Be sure to add the standby load of the FPO board to the DC1 Current (See the instruction manual for the standby load of the FPO model you are using).
Step 2: | Enter the alarm load values in to the red cells in the "Alarm Load" box. If there is no Alarm Current, leave these cells blank.
Step 3: | Enter the required Alarm time and the desired battery size into the red and purple cells in the "Battery Size & Required Alarm Time" box. If there is no Alarm Time, leave these cells blank.
Step 4: | Click the blue "Calculate" button. The recommended battery size appears in the green cell in the "Results" box.
Note: | This calculator gives the "ideal" standby time and does not factor in the decreasing AH capacity of a battery as it ages. In order to ensure adequate standby time throughout the battery's life, a 20% margin should be added to battery size.
Back

## Voltage Drop Calc
Voltage Drop Calculator
General Information |  |  |  | Wire Run Information
| Start Voltage |  | Volts |  | Wire Length (One Way) |  | Feet
| Temperature | 75 | Deg. F. |  | Wire Gauge |  | AWG
| Allowable Drop | 10 | % |  | Current through Wire Run |  | Amps
| Low Battery | 10.2 | Volts
Results
[5 empty] | Wire Resistance | 0 | Ohms
[5 empty] | Voltage Drop | 0 | Volts
[5 empty] | End Voltage | 0 | Volts
[5 empty] | % Drop | Error | %
[5 empty] | End Voltage at Low battery | 10.2 | Volts
Notes:
Job:
Location:
Power Supply ID:
Date: | 2014-12-15
Help
Help
Calculate
Main Menu

## Voltage Drop Help
Help for Voltage Drop Calculator
The Voltage Drop Calculator calculates the voltage through a given wire run based on wire size, length, load current, and other factors.
Step 1: | Enter the starting voltage, ambient temperature in degrees fahernheit, and allowable voltage drop in percentage into the cells in the "General Information" box. Use 75 degrees if the ambient temperature is not known.
Step 2: | Enter the wire length in feet, wire gauge in AWG, and current drawn through the wire in amps into the "Wire Run Information" box. The wire length should be entered as a "one way" length and should not be doubled to account for source and return wires.
Step 3: | Click the blue "Calculate" button. The results appear in the "Results" box. The "End Voltage at Low Battery" cell gives the voltage the load will see when the battery set is fully discharged (by UL definition).
Note: | This calculator is intended for use with solid wire only.
Note: | This calculator assumes one bulk load at the end of the wire run. Distributed loads (with loads at different points along the wire run) can be calculated one of two ways with this calculator. The voltage drop can be calculated as if the entire load is at the end of the wire run, however this will give a much higher voltage drop than you will see in the real world. The other method involves breaking the wire run into sections, each calculated independently. The entire current will be drawn through the first section. For the second section, the first load value will be subtracted from the total load and the ending voltage of the first section will be used as the starting voltage. This will be continued until all sections are calculated.
Back

## Wire Size Calc
Wire Size Calculator
General Information |  |  |  | Wire Run Information
| Start Voltage |  | Volts |  | Wire Length (One Way) |  | Feet
| Temperature | 75 | Deg. F. |  | Current through Wire Run |  | Amps
| Allowable Drop | 10 | %
| Low Battery | 10.2 | Volts
Results
[5 empty] | Max Voltage Drop | 0 | Volts
[5 empty] | Max. Wire Resistance | Error | Ohms
[5 empty] | Minimum Wire Gauge Req. | Error | AWG
[5 empty] | Actual Wire Resistance | Error | Ohms
[5 empty] | End Voltage | Error | Volts
[5 empty] | End Voltage at Low Battery | Error | Volts
Notes:
Job:
Location:
Power Supply ID:
Date: | 2014-12-15
Help
Help
Calculate
Main Menu

## Wire Size Help
Help for Wire Size Calculator
The Voltage Drop Calculator calculates the voltage through a given wire run based on wire size, length, load current, and other factors.
Step 1: | Enter the starting voltage, ambient temperature in degrees fahernheit, and allowable voltage drop in percentage into the cells in the "General Information" box. Use 75 degrees if the ambient temperature is not known.
Step 2: | Enter the wire length in feet and current drawn through the wire in amps into the "Wire Run Information" box. The wire length should be entered as a "one way" length and should not be doubled to account for source and return wires.
Step 3: | Click the blue "Calculate" button. The results appear in the "Results" box. The "End Voltage" cell gives the voltage the load will see if the recommended wire size is used. The "End Voltage at Low Battery" cell gives the voltage the load will see when the battery set is fully discharged (by UL definition).
Note: | The Min. Wire Gauge Required is the theoretical minimum wire gauge required to maintain an end voltage within the percentage entered. Round up to the next standard wire gauge if a non-standard wire gauge is indicated.
Note: | A negative number in the Min. Wire Gauge Required cell indicates a required wire larger than AWG 0. A result of -1 converts to AWG 00, a result of -2 converts to AWG 000, and so on.
Back

## Ohms Law Calc
Ohm's Law Calculators
Current Calculation |  |  |  |  | Voltage Calculation
| Resistance |  | Ohms |  |  | Current |  | Amps
| Voltage |  | Volts |  |  | Resistance |  | Ohms
| Power |  | Watts |  |  | Power |  | Watts
| Current | Error | Amps |  |  | Voltage | 0 | Volts
Resistance Calculation |  |  |  |  | Power Calculation
| Voltage |  | Volts |  |  | Voltage |  | Volts
| Current |  | Amps |  |  | Current |  | Amps
| Power |  | Watts |  |  | Resistance |  | Ohms
| Resistance | Error | Ohms |  |  | Power | 0 | Watts
Notes:
Job:
Location:
Power Supply ID:
Date: | 2014-12-15
Help
Help
Calculate
Main Menu

## Ohms Law Help
Help for Ohm's Law Calculators
The Ohm's Law Calculators calculate Voltage, Current, Resistance, or Power in a circuit given two parameters.
Step 1: | Locate the calculator required to obtain the desired result on the page
Step 2: | Enter any two of the parameters required in the blue cells for that calculator. Do not enter all three parameters or an error will occur.
Step 3: | Click the blue "Calculate" button. The results appear in the green cell.
Note: | If the green cell says "Error", ensure that only two blue cells are used, and that valid numbers are entered into them. If "Error" remains, verify that the numbers are not causing a divide by zero to occur.
Back

## Misc Calcs
Miscellaneous Calculators
Power Supply BTU |  |  |  | Temp. Conversion |  |  | Length Conversion |  |  | Resistors in Series
Pin |  | W |  | Deg F |  |  | Inches |  |  | R1 |  | Ohms
Pout |  | W |  | Deg C | -17.7778 |  | cm | 0 |  | R2 |  | Ohms
BTU | 0 | BTU | [7 empty] | R3 |  | Ohms
|  |  |  | Deg C |  |  | cm |  |  | R4 |  | Ohms
|  |  |  | Deg F | 32 |  | Inches | 0 |  | R Total | 0 | Ohms
Efficiency
Pin |  | W
Pout |  | W |  | Weight Conversion | [5 empty] | Resistors In Parallel
Efficiency | Error | % |  | Lbs. | [5 empty] | R1 |  | Ohms
|  |  |  | kg | 0 |  |  |  |  | R2 |  | Ohms
[10 empty] | R3 |  | Ohms
Power Factor |  |  |  | kg | [5 empty] | R4 |  | Ohms
Pmeas. |  | W |  | Lbs. | 0 |  |  |  |  | R Total | Error | Ohms
Vmeas. |  | V
Imeas. |  | A
PF | Error
Notes:
Job:
Location:
Power Supply ID:
Date: | 2014-12-15
Help
Help
Calculate
Main Menu

## Misc Calcs Help
Help for Miscellaneous Calculators
BTU: | Enter the input and output power in the blue cells and click "Calculate" - the calculated BTU is in the green cell
Efficiency: | Enter the input and output power into the blue cells and click "Calculate" - the calculated efficiency is in the green cell
Power Factor: | Enter the measured input power and the measured input voltage and current into the blue calls and click "Calculate" - the calculated Power Factor is in the green cell.
Temp Conversion: | Enter the starting temperature into the appropriate blue cell and click "Calculate" - the converted temperature is in the corresponding green cell
Weight Conversion: | Enter the starting weight into the appropriate blue cell and click "Calculate" - the converted weight is in the corresponding green cell
Length Conversion: | Enter the starting length into the appropriate blue cell and click "Calculate" - the converted length is in the corresponding green cell
Series Resistors: | Enter up to four resistor values into the blue cells and click "Calculate" - the total series resistance is in the green cell.
Parallel Resistors: | Enter up to four resistor values into the blue cells and click "Calculate" - the total parallel resistance is in the green cell.
Back

## B100 Calculator
B100 Calculator
[5 empty] | Input Voltage | 24 | V
[5 empty] | Output Voltage | 12 | V
[5 empty] | Output Load | 2 | A
[5 empty] | Draw from Input Power Supply | 1.15 | A
[6 empty] | 27.6 | W
Available Remaining Power When Using FPO
|  | FPO75 |  | FPO150 |  | FPO250
|  | 47.4 | W | 122.4 | W | 222.4 | W
Available Remaining FPO Amps
|  | 1.85 | A | 4.85 | A | 8.85 | A
|  | Step 1: | Enter the input voltage of the B100 in VOLTS
|  | Step 2: | Enter the output voltage setting of the B100 in VOLTS
|  | Step 3: | Enter the Output load of the B100 in AMPS
|  | Step 4: | Get results in AMPS, in Watts
Notes:
Job:
Location:
Power Supply ID:
Date: | 2014-12-15
Help
Help
Calculate
Main Menu

## B100 Calcs Help
Help for B100 Calculator
The B100 Calculator determines the current & power draw from the FPO power supply as well as the remaining current and power available from the FPO power supply.
Step 1: | Enter the input voltage of the B100 in VOLTS
Step 2: | Enter the output voltage of the B100 in VOLTS
Step 3: | Enter the output load of the B100 in AMPS
Step 4: | Get results in AMPS and WATTS
Back

## C8 Config Tool
C4/C8 Configuration Tool
| Voltage Sources |  |  |  |  | Jumper Settings
|  | B1 |  | V |  |  | Jumper | Position
|  | B2 |  | V |  |  | A | 1
[7 empty] | B | 1
[7 empty] | C |  | 2
| Zone Information | [5 empty] | D | 1
[7 empty] | E |  | 2
[7 empty] | F |  | 2
|  | Input Type | NC Dry Contact
|  | Output Type | Mag Lock
Output Voltage
|  | Zone FAI? | Yes
Notes:
Job:
Location:
Power Supply ID:
Date: | 2014-12-15
Help
Main Menu
Help

## C8 Config Tool Help
Help for C8 Configuration Tool
The C8 Configuratin Tool determines the correct jumper settings for a single zone of a C4, C4P, C8, or C8P based on
configuration information entered.
Step 1: | Under "Voltage Sources", enter the Buss 1 and Buss 2 (if used) voltages for the system. The Buss 1 power
supply connects to the B1 power input of the C4/C8. The Buss 2 power supply connects to B2.
Step 2: | Enter the configuration information under "Zone Information" using the drop down boxes.
|  | Input Type | The method used for activating the zone. Options include NO or NC dry contact,
voltage application or removal, open collector, or no input (for a constant output).
|  | Output Type | The desired output device or configuration. Options include Mag Lock, Fail Safe or
Secure Strike, NO or NC Relay Contact, or Constant Output.
|  | Output Voltage | The output voltage for the zone, based upon the voltages entered in the Voltage
Sources block.
|  | Zone FAI? | Determines whether or not FAI activation will affect the zone. Options are Yes or No.
Step 3: | Review the jumper settings in the "Jumper Settings" block on the right side of the screen.
Back